## Substations
Notes:
Substations with a Primary Voltage >=110KV only
Transformers ratings should be nominal nameplate at highest continuous rating - i.e with pumps / fans on where applicable
Substation | Voltage Ratio |  | Number of Transformers | Transformer Ratings |  |  |  | "N" Rating | "N-1" Rating | Summer Peak Load * | * Load at 1500hrs 18/1/2010 - date / time of last Summer network maximum demand (8891 MW).
|  |  |  | MVA |  |  |  | MVA | MVA | MVA
H001 | 275 | 110 | 2 | 250 | 200 |  |  | 450 | 200 | 157
H002E | 275 | 110 | 2 | 250 | 375 |  |  | 625 | 250 | 306
H002W | 275 | 110 | 3 | 375 | 375 | 375 |  | 1125 | 750 | 711
H003 | 275 | 110 | 4 | 250 | 250 | 375 | 375 | 1250 | 875 | 531
H004 | 275 | 110 | 3 | 250 | 250 | 250 |  | 750 | 500 | 376
H005 | 275 | 132 | 3 | 120 | 120 | 275 |  | 515 | 240 | 196
H006 | 275 | 132 | 2 | 250 | 250 |  |  | 500 | 250 | 140
H007 | 275 | 132 | 2 | 300 | 300 |  |  | 600 | 300 | 180
H009 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 343
H009 | 132/ | 110 | 3 | 120 | 140 |  |  | 260 | 120 | 76
H010 | 275 | 132 | 3 | 200 | 200 |  |  | 400 | 200 | 162
H011 | 275 | 132 | 3 | 200 | 200 | 250 |  | 650 | 400 | 338
H013 | 275 | 132 | 3 | 250 | 250 | 250 |  | 750 | 500 | 116
H014 | 275 | 110 | 3 | 250 | 200 | 200 |  | 650 | 400 | 83
H014 | 330 | 275 | 2 | 1500 | 1500 |  |  | 3000 | 1500 | 1189
H015 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 218
H016 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 427
H018 | 275 | 132 | 2 | 90 | 90 |  |  | 180 | 90 | 28
H021 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 421
H022 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 447
H024 | 275 | 132 | 1 | 250 |  |  |  | 250 | 0 | 146
H031 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 435
H032 | 275 | 132 | 2 | 200 | 200 |  |  | 400 | 200 | 59
H035 | 275 | 132 | 1 | 375 |  |  |  | 375 | 0 | 26
H038 | 275 | 110 | 1 | 375 |  |  |  | 375 | 0 | 186
H039 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 191
H058 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 81
H062 | 275 | 110 | 1 | 375 |  |  |  | 375 | 0 | 194
H063 | 275 | 132 | 2 | 350 | 350 |  |  | 700 | 350 | 118
R002 | 330 | 275 | 2 | 1125 | 1125 |  |  | 2250 | 1125 | 440
R003 | 330 | 132 | 1 | 100 |  |  |  | 100 | 0 | 12
[8 empty] | 22530 | 11250 | 8333
[8 empty] | 0.36986 | 0.74071

## Shared Lines
Notes:
Lines >=110KV only
Ratings ratings should be nominal based on "nominal" wind / temperature design
|  |  | Nominal Rating |  | Non Thermal | Load at last Summer Peak * | * Load at 1500hrs 18/1/2010 - date / time of last Summer network maximum demand (8891 MW).
Line | Voltage | Length (km) | Summer (MVA) | Winter (MVA) | Rating Constraints | Load (MVA)
Line 1 | 110 | 7.3 | 144 | 159 | No | 111 | 77.08% |  | 0%
Line 2 | 110 | 4.5 | 144 | 159 | No | 8 | 5.556% |  | 0%
Line 3 | 110 | 19.3 | 144 | 159 | No | 62 | 43.06% | 1 | 1.389%
Line 4 | 110 | 12.1 | 144 | 159 | No | 44 | 30.56% | 2 | 1.478%
Line 5 | 110 | 6.1 | 144 | 159 | No | 48 | 33.33% | 3 | 1.724%
Line 6 | 110 | 4.9 | 144 | 159 | No | 5 | 3.472% | 4 | 1.97%
Line 7 | 110 | 8.3 | 144 | 159 | No | 4 | 2.778% | 5 | 2.26%
Line 8 | 110 | 12.5 | 137 | 153 | No | 89 | 64.96% | 6 | 2.778%
Line 9 | 110 | 12.5 | 137 | 153 | No | 88 | 64.23% | 7 | 3.472%
Line 10 | 110 | 34.4 | 218 | 248 | No | 127 | 58.26% | 8 | 3.521%
Line 11 | 110 | 34.4 | 218 | 248 | No | 126 | 57.8% | 9 | 4%
Line 12 | 110 | 7.6 | 144 | 159 | No | 18 | 12.5% | 10 | 5.556%
Line 13 | 110 | 19.1 | 184 | 206 | No | 13 | 7.065% | 11 | 5.607%
Line 14 | 110 | 13.1 | 131 | 143 | No | 10 | 7.634% | 12 | 5.634%
Line 15 | 110 | 13.1 | 131 | 143 | No | 10 | 7.634% | 13 | 6.066%
Line 16 | 132 | 15.8 | 383 | 425 | No | 82 | 21.41% | 14 | 7.065%
Line 17 | 132 | 3.8 | 383 | 425 | No | 86 | 22.45% | 15 | 7.299%
Line 18 | 110 | 12.2 | 144 | 159 | No | 48 | 33.33% | 16 | 7.299%
Line 19 | 110 | 17.4 | 144 | 159 | No | 34 | 23.61% | 17 | 7.362%
Line 20 | 132 | 67.7 | 137 | 159 | No | 15 | 10.95% | 18 | 7.443%
Line 21 | 110 | 7.7 | 144 | 159 | No | 44 | 30.56% | 19 | 7.609%
Line 22 | 110 | 19.1 | 184 | 206 | No | 14 | 7.609% | 20 | 7.634%
Line 23 | 275 | 23.5 | 1150 | 1285 | No | 399 | 34.7% | 21 | 7.634%
Line 24 | 275 | 16.2 | 506 | 592 | No | 168 | 33.2% | 22 | 8.01%
Line 25 | 275 | 16.6 | 506 | 592 | No | 171 | 33.79% | 23 | 9.602%
Line 26 | 275 | 159.6 | 799 | 885 | No | 64 | 8.01% | 24 | 9.756%
Line 27 | 275 | 77.5 | 799 | 885 | No | 143 | 17.9% | 25 | 9.756%
Line 28 | 275 | 51.8 | 656 | 763 | No | 166 | 25.3% | 26 | 9.859%
Line 29 | 275 | 95.7 | 799 | 885 | No | 203 | 25.41% | 27 | 9.989%
Line 30 | 275 | 44.5 | 496 | 568 | No | 114 | 22.98% | 28 | 10.13%
Line 31 | 275 | 99.6 | 482 | 556 | No | 86 | 17.84% | 29 | 10.56%
Line 32 | 275 | 135.6 | 799 | 885 | No | 276 | 34.54% | 30 | 10.56%
Line 33 | 275 | 152.2 | 799 | 885 | No | 246 | 30.79% | 31 | 10.66%
Line 34 | 275 | 148.9 | 763 | 848 | No | 177 | 23.2% | 32 | 10.95%
Line 35 | 275 | 149.9 | 763 | 848 | No | 177 | 23.2% | 33 | 11.24%
Line 36 | 275 | 50.6 | 656 | 763 | No | 394 | 60.06% | 34 | 11.81%
Line 37 | 275 | 17.4 | 799 | 885 | No | 404 | 50.56% | 35 | 11.95%
Line 38 | 275 | 139.8 | 799 | 885 | No | 217 | 27.16% | 36 | 12.36%
Line 39 | 275 | 143.8 | 471 | 543 | No | 139 | 29.51% | 37 | 12.5%
Line 40 | 275 | 292.4 | 471 | 542 | No | 126 | 26.75% | 38 | 12.5%
Line 41 | 275 | 169.3 | 941 | 1085 | No | 94 | 9.989% | 39 | 12.59%
Line 42 | 275 | 35.7 | 1401 | 1496 | No | 494 | 35.26% | 40 | 13.07%
Line 43 | 275 | 100.8 | 763 | 848 | No | 215 | 28.18% | 41 | 13.67%
Line 44 | 275 | 131.4 | 1088 | 1242 | No | 503 | 46.23% | 42 | 13.94%
Line 45 | 275 | 21.9 | 852 | 931 | No | 48 | 5.634% | 43 | 13.95%
Line 46 | 275 | 11.2 | 847 | 957 | No | 217 | 25.62% | 44 | 14.15%
Line 47 | 275 | 106.9 | 523 | 587 | No | 53 | 10.13% | 45 | 14.61%
Line 48 | 275 | 130 | 1045 | 1173 | No | 533 | 51% | 46 | 14.8%
Line 49 | 275 | 108.5 | 440 | 525 | No | 114 | 25.91% | 47 | 14.92%
Line 50 | 275 | 151.5 | 788 | 960 | No | 182 | 23.1% | 48 | 15%
Line 51 | 275 | 65.2 | 506 | 592 | No | 190 | 37.55% | 49 | 15.49%
Line 52 | 275 | 65.3 | 506 | 592 | No | 193 | 38.14% | 50 | 15.73%
Line 53 | 275 | 108.3 | 1088 | 1242 | No | 513 | 47.15% | 51 | 16.07%
Line 54 | 275 | 35.7 | 656 | 763 | No | 254 | 38.72% | 52 | 16.26%
Line 55 | 275 | 17.6 | 934 | 1104 | No | 300 | 32.12% | 53 | 16.26%
Line 56 | 275 | 17.6 | 934 | 1104 | No | 288 | 30.84% | 54 | 16.33%
Line 57 | 275 | 108.6 | 544 | 621 | No | 110 | 20.22% | 55 | 16.34%
Line 58 | 275 | 127.5 | 880 | 1049 | No | 264 | 30% | 56 | 16.57%
Line 59 | 275 | 244.1 | 467 | 552 | No | 133 | 28.48% | 57 | 17%
Line 60 | 275 | 244.1 | 467 | 552 | No | 133 | 28.48% | 58 | 17.51%
Line 61 | 275 | 7.1 | 934 | 1104 | No | 271 | 29.01% | 59 | 17.53%
Line 62 | 275 | 7.6 | 934 | 1104 | No | 259 | 27.73% | 60 | 17.84%
Line 63 | 275 | 94.7 | 544 | 621 | No | 340 | 62.5% | 61 | 17.9%
Line 64 | 275 | 131.4 | 1088 | 1242 | No | 508 | 46.69% | 62 | 18.56%
Line 65 | 275 | 137.4 | 739 | 849 | No | 101 | 13.67% | 63 | 18.68%
Line 66 | 275 | 137.1 | 739 | 849 | No | 103 | 13.94% | 64 | 18.72%
Line 67 | 275 | 161.8 | 1088 | 1242 | No | 61 | 5.607% | 65 | 18.77%
Line 68 | 275 | 167.8 | 854 | 953 | No | 82 | 9.602% | 66 | 19.01%
Line 69 | 132 | 3.2 | 97 | 111 | No | 17 | 17.53% | 67 | 19.23%
Line 70 | 132 | 3.2 | 97 | 111 | No | 32 | 32.99% | 68 | 19.44%
Line 71 | 132 | 3.2 | 97 | 111 | No | 32 | 32.99% | 69 | 19.48%
Line 72 | 132 | 86.6 | 142 | 163 | No | 15 | 10.56% | 70 | 19.51%
Line 73 | 132 | 86.6 | 142 | 163 | No | 5 | 3.521% | 71 | 19.51%
Line 74 | 132 | 22.2 | 89 | 103 | No | 51 | 57.3% | 72 | 20.22%
Line 75 | 132 | 22.3 | 89 | 103 | No | 54 | 60.67% | 73 | 20.35%
Line 76 | 132 | 16.2 | 84 | 98 | No | 38 | 45.24% | 74 | 20.42% | 0.35407
Line 77 | 132 | 62.1 | 84 | 98 | No | 56 | 66.67% | 75 | 20.56%
Line 78 | 132 | 78.7 | 129 | 137 | No | 63 | 48.84% | 76 | 20.83%
Line 79 | 132 | 41.4 | 93 | 106 | No | 26 | 27.96% | 77 | 20.93%
Line 80 | 132 | 133.4 | 93 | 106 | No | 33 | 35.48% | 78 | 21.21%
Line 81 | 132 | 133.5 | 145 | 168 | No | 40 | 27.59% | 79 | 21.28%
Line 82 | 132 | 37.3 | 203 | 230 | No | 4 | 1.97% | 80 | 21.41%
Line 83 | 132 | 60.7 | 134 | 158 | No | 41 | 30.6% | 81 | 21.43%
Line 84 | 132 | 92.4 | 134 | 158 | No | 46 | 34.33% | 82 | 21.5%
Line 85 | 132 | 76.8 | 134 | 159 | No | 49 | 36.57% | 83 | 22.31%
Line 86 | 132 | 69.3 | 134 | 159 | No | 47 | 35.07% | 84 | 22.45%
Line 87 | 132 | 90.6 | 82 | 97 | No | 16 | 19.51% | 85 | 22.98%
Line 88 | 132 | 86 | 82 | 97 | No | 16 | 19.51% | 86 | 23.1%
Line 89 | 132 | 75.1 | 130 | 145 | No | 29 | 22.31% | 87 | 23.15%
Line 90 | 132 | 203.9 | 84 | 98 | No | 22 | 26.19% | 88 | 23.2%
Line 91 | 132 | 203.9 | 84 | 98 | No | 21 | 25% | 89 | 23.2%
Line 92 | 132 | 6.4 | 153 | 172 | No | 0 | 0% | 90 | 23.33%
Line 93 | 132 | 110.7 | 153 | 172 | No | 20 | 13.07% | 91 | 23.33%
Line 94 | 132 | 68.9 | 108 | 127 | No | 26 | 24.07% | 92 | 23.6%
Line 95 | 132 | 70.5 | 108 | 127 | No | 26 | 24.07% | 93 | 23.61%
Line 96 | 132 | 139.6 | 88 | 103 | No | 45 | 51.14% | 94 | 23.75%
Line 97 | 132 | 93.2 | 203 | 230 | No | 47 | 23.15% | 95 | 24.07%
Line 98 | 132 | 45.6 | 89 | 103 | No | 31 | 34.83% | 96 | 24.07%
Line 99 | 132 | 70.6 | 177 | 204 | No | 4 | 2.26% | 97 | 24.79%
Line 100 | 132 | 13.5 | 89 | 103 | No | 21 | 23.6% | 98 | 25%
Line 101 | 132 | 13.5 | 89 | 103 | No | 10 | 11.24% | 99 | 25.24%
Line 102 | 132 | 17.7 | 182 | 203 | No | 35 | 19.23% | 100 | 25.3%
Line 103 | 132 | 23.7 | 397 | 433 | No | 237 | 59.7% | 101 | 25.41%
Line 104 | 132 | 23.7 | 397 | 433 | No | 241 | 60.71% | 102 | 25.62%
Line 105 | 132 | 3.3 | 97 | 111 | No | 18 | 18.56% | 103 | 25.73%
Line 106 | 132 | 72.9 | 182 | 199 | No | 59 | 32.42% | 104 | 25.74%
Line 107 | 132 | 17.7 | 182 | 198 | No | 34 | 18.68% | 105 | 25.81%
Line 108 | 132 | 37 | 142 | 167 | No | 22 | 15.49% | 106 | 25.86%
Line 109 | 132 | 48.6 | 82 | 97 | No | 8 | 9.756% | 107 | 25.91%
Line 110 | 132 | 19.8 | 217 | 253 | No | 88 | 40.55% | 108 | 26.13%
Line 111 | 132 | 0.9 | 295 | 328 | No | 152 | 51.53% | 109 | 26.19%
Line 112 | 132 | 99.7 | 150 | 176 | No | 35 | 23.33% | 110 | 26.39%
Line 113 | 132 | 99.7 | 150 | 176 | No | 35 | 23.33% | 111 | 26.39%
Line 114 | 132 | 19.4 | 70 | 89 | No | 15 | 21.43% | 112 | 26.52%
Line 115 | 132 | 12.2 | 382 | 424 | No | 78 | 20.42% | 113 | 26.75%
Line 116 | 132 | 12.1 | 100 | 114 | No | 15 | 15% | 114 | 26.85%
Line 117 | 132 | 0.9 | 66 | 85 | No | 14 | 21.21% | 115 | 27.08%
Line 118 | 132 | 17.9 | 77 | 96 | No | 28 | 36.36% | 116 | 27.16%
Line 119 | 132 | 27.7 | 72 | 90 | No | 29 | 40.28% | 117 | 27.27%
Line 120 | 132 | 9.3 | 72 | 90 | No | 19 | 26.39% | 118 | 27.59%
Line 121 | 132 | 65.9 | 72 | 90 | No | 14 | 19.44% | 119 | 27.73%
Line 122 | 132 | 38 | 72 | 90 | No | 15 | 20.83% | 120 | 27.96%
Line 123 | 132 | 7.2 | 112 | 125 | No | 18 | 16.07% | 121 | 28.18%
Line 124 | 132 | 7.2 | 112 | 125 | No | 14 | 12.5% | 122 | 28.41%
Line 125 | 110 | 4.5 | 151 | 170 | No | 59 | 39.07% | 123 | 28.47%
Line 126 | 110 | 4.5 | 151 | 170 | No | 61 | 40.4% | 124 | 28.48%
Line 127 | 132 | 0.8 | 72 | 90 | No | 1 | 1.389% | 125 | 28.48%
Line 128 | 132 | 104.8 | 153 | 172 | No | 25 | 16.34% | 126 | 29.01%
Line 129 | 110 | 4.5 | 151 | 170 | No | 66 | 43.71% | 127 | 29.51%
Line 130 | 132 | 12.1 | 89 | 103 | No | 70 | 78.65% | 128 | 29.86%
Line 131 | 132 | 1.2 | 107 | 118 | No | 22 | 20.56% | 129 | 30%
Line 132 | 132 | 1.2 | 107 | 118 | No | 23 | 21.5% | 130 | 30.56%
Line 133 | 132 | 1.2 | 108 | 127 | No | 47 | 43.52% | 131 | 30.56%
Line 134 | 132 | 4.9 | 142 | 167 | No | 15 | 10.56% | 132 | 30.6%
Line 135 | 132 | 4.9 | 142 | 167 | No | 14 | 9.859% | 133 | 30.79%
Line 136 | 132 | 19.4 | 134 | 159 | No | 82 | 61.19% | 134 | 30.84%
Line 137 | 132 | 3.8 | 88 | 103 | No | 24 | 27.27% | 135 | 31.04%
Line 138 | 132 | 3.8 | 88 | 103 | No | 25 | 28.41% | 136 | 31.29%
Line 139 | 110 | 6.9 | 323 | 367 | No | 146 | 45.2% | 137 | 32.12%
Line 140 | 110 | 6.8 | 323 | 367 | No | 139 | 43.03% | 138 | 32.42%
Line 141 | 132 | 17.4 | 406 | 459 | No | 109 | 26.85% | 139 | 32.99%
Line 142 | 132 | 31.6 | 134 | 159 | No | 55 | 41.04% | 140 | 32.99%
Line 143 | 132 | 45.6 | 89 | 103 | No | 11 | 12.36% | 141 | 33.2%
Line 144 | 132 | 23.2 | 203 | 230 | No | 33 | 16.26% | 142 | 33.33%
Line 145 | 132 | 37.9 | 203 | 230 | No | 33 | 16.26% | 143 | 33.33%
Line 146 | 110 | 8.5 | 235 | 250 | No | 97 | 41.28% | 144 | 33.79%
Line 147 | 110 | 8.5 | 235 | 250 | No | 98 | 41.7% | 145 | 34.03%
Line 148 | 110 | 28.3 | 125 | 146 | No | 61 | 48.8% | 146 | 34.33%
Line 149 | 132 | 0.1 | 200 | 224 | No | 71 | 35.5% | 147 | 34.54%
Line 150 | 132 | 0.2 | 200 | 224 | No | 8 | 4% | 148 | 34.7%
Line 151 | 132 | 32.9 | 181 | 204 | No | 30 | 16.57% | 149 | 34.83%
Line 152 | 132 | 22.7 | 181 | 204 | No | 27 | 14.92% | 150 | 35.07%
Line 153 | 132 | 6 | 177 | 204 | No | 31 | 17.51% | 151 | 35.26%
Line 154 | 110 | 11 | 342 | 381 | No | 88 | 25.73% | 152 | 35.48%
Line 155 | 110 | 11.3 | 342 | 381 | No | 107 | 31.29% | 153 | 35.5%
Line 156 | 110 | 5.5 | 144 | 159 | No | 38 | 26.39% | 154 | 35.82%
Line 157 | 110 | 12.2 | 144 | 159 | No | 39 | 27.08% | 155 | 36.13%
Line 158 | 110 | 7.8 | 144 | 159 | No | 43 | 29.86% | 156 | 36.36%
Line 159 | 110 | 7.7 | 144 | 159 | No | 41 | 28.47% | 157 | 36.57%
Line 160 | 110 | 3.6 | 144 | 159 | No | 17 | 11.81% | 158 | 37.55%
Line 161 | 132 | 26.1 | 129 | 146 | No | 27 | 20.93% | 159 | 38.14%
Line 162 | 132 | 134.8 | 205 | 229 | No | 0 | 0% | 160 | 38.14%
Line 163 | 132 | 11 | 420 | 480 | No | 106 | 25.24% | 161 | 38.72%
Line 164 | 132 | 69.1 | 134 | 159 | No | 48 | 35.82% | 162 | 39.07%
Line 165 | 132 | 88.2 | 142 | 167 | No | 57 | 40.14% | 163 | 40.14%
Line 166 | 132 | 53.6 | 82 | 97 | No | 8 | 9.756% | 164 | 40.28%
Line 167 | 132 | 68 | 141 | 158 | No | 30 | 21.28% | 165 | 40.4%
Line 168 | 110 | 9.4 | 144 | 159 | No | 49 | 34.03% | 166 | 40.55%
Line 169 | 132 | 10.2 | 203 | 230 | No | 38 | 18.72% | 167 | 41.04%
Line 170 | 132 | 32.5 | 406 | 459 | No | 6 | 1.478% | 168 | 41.28%
Line 171 | 132 | 32.5 | 406 | 459 | No | 7 | 1.724% | 169 | 41.7%
Line 172 | 132 | 57.5 | 129 | 146 | No | 18 | 13.95% | 170 | 41.9%
Line 173 | 132 | 9.4 | 548 | 622 | No | 40 | 7.299% | 171 | 43.03%
Line 174 | 132 | 9.4 | 548 | 622 | No | 40 | 7.299% | 172 | 43.06%
Line 175 | 275 | 333.5 | 1088 | 1242 | No | 159 | 14.61% | 173 | 43.52%
Line 176 | 275 | 333.5 | 1088 | 1242 | No | 161 | 14.8% | 174 | 43.71%
Line 177 | 275 | 108.3 | 1096 | 1231 | No | 515 | 46.99% | 175 | 45.2%
Line 178 | 275 | 26.3 | 847 | 957 | No | 483 | 57.02% | 176 | 45.24%
Line 179 | 275 | 129.2 | 1088 | 1242 | No | 569 | 52.3% | 177 | 46.23%
Line 180 | 275 | 129.2 | 1088 | 1242 | No | 561 | 51.56% | 178 | 46.69%
Line 181 | 275 | 22.7 | 700 | 822 | No | 267 | 38.14% | 179 | 46.99%
Line 182 | 275 | 16.3 | 656 | 763 | No | 237 | 36.13% | 180 | 47.15%
Line 183 | 275 | 28.2 | 1030 | 1186 | No | 654 | 63.5% | 181 | 47.65%
Line 184 | 275 | 37.3 | 1150 | 1285 | No | 224 | 19.48% | 182 | 48.8%
Line 185 | 275 | 36.5 | 852 | 931 | No | 357 | 41.9% | 183 | 48.84%
Line 186 | 275 | 30 | 1150 | 1285 | No | 357 | 31.04% | 184 | 49.11%
Line 187 | 275 | 57.2 | 847 | 957 | No | 218 | 25.74% | 185 | 50.56%
Line 188 | 275 | 57.2 | 847 | 957 | No | 219 | 25.86% | 186 | 51%
Line 189 | 275 | 11.1 | 656 | 763 | No | 355 | 54.12% | 187 | 51.14%
Line 190 | 275 | 0.2 | 1141 | 1295 | No | 194 | 17% | 188 | 51.53%
Line 191 | 275 | 127.5 | 1141 | 1295 | No | 271 | 23.75% | 189 | 51.56%
Line 192 | 275 | 11.3 | 847 | 957 | No | 210 | 24.79% | 190 | 52.3%
Line 193 | 275 | 33.4 | 656 | 763 | No | 174 | 26.52% | 191 | 54.12%
Line 194 | 275 | 31.1 | 1150 | 1285 | No | 234 | 20.35% | 192 | 57.02%
Line 195 | 275 | 162.1 | 1088 | 1242 | No | 66 | 6.066% | 193 | 57.26%
Line 196 | 275 | 152.3 | 1088 | 1242 | No | 130 | 11.95% | 194 | 57.3%
Line 197 | 275 | 152.4 | 1088 | 1242 | No | 137 | 12.59% | 195 | 57.35%
Line 198 | 275 | 108.1 | 1088 | 1242 | No | 623 | 57.26% | 196 | 57.8%
Line 199 | 275 | 107.9 | 1088 | 1242 | No | 624 | 57.35% | 197 | 58.26%
Line 200 | 275 | 49.1 | 763 | 848 | No | 108 | 14.15% | 198 | 59.7%
Line 201 | 275 | 179.5 | 807 | 918 | No | 86 | 10.66% | 199 | 60.06%
Line 202 | 275 | 179.5 | 496 | 568 | No | 81 | 16.33% | 200 | 60.67%
Line 203 | 275 | 13.6 | 496 | 568 | No | 78 | 15.73% | 201 | 60.71%
Line 204 | 330 | 91.3 | 1236 | 1423 | No | 235 | 19.01% | 202 | 61.19%
Line 205 | 330 | 91.3 | 1236 | 1423 | No | 232 | 18.77% | 203 | 62.5%
Line 206 | 330 | 45.4 | 1236 | 1423 | No | 323 | 26.13% | 204 | 63.5%
Line 207 | 330 | 45.5 | 1236 | 1423 | No | 319 | 25.81% | 205 | 64.23%
Line 208 | 330 | 94.5 | 1236 | 1423 | No | 607 | 49.11% | 206 | 64.96%
Line 209 | 330 | 94.5 | 1236 | 1423 | No | 589 | 47.65% | 207 | 66.67%
Line 210 | 330 | 115.3 | 1236 | 1423 | No | 91 | 7.362% | 208 | 77.08%
Line 211 | 330 | 115.3 | 1236 | 1423 | No | 92 | 7.443% | 209 | 78.65%
|  | 12494.8 | [5 empty] | Mean | 28.1%
|  |  | 442.6351 | [5 empty] | 28.1%