## Substations
Notes:
Substations with a Primary Voltage >=110KV only
Transformers ratings should be nominal nameplate at highest continuous rating - i.e with pumps / fans on where applicable
Substation | Voltage Ratio | Number of Transformers | Transformer Ratings | "N" Rating | "N-1" Rating |  | Summer Peak Load | Winter Peak Load | Customer Connection/Shared Network Asset | n |  | n
|  |  | MVA | MVA | MVA |  | MVA | MVA |  | Summer |  | Summer
Substation 1 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 163.4309 | 147.374 | Shared Network Asset | 21.79% | 1 | 6.359% | 1
Substation 2 | 525/345/34.5 | 2 | 1500/1500 | 3000 | 1500 | 2 | 361.4909 | 325.975 | Shared Network Asset | 12.05% | 2 | 9.276% | 2
Substation 3 | 525/345/34.5 | 2 | 1500/1500 | 3000 | 1500 | 2 | 1139.3731 | 1027.4315 | Shared Network Asset | 37.98% | 3 | 11.36% | 3
Substation 4 | 330/138.6/11 | 3 | 375/375/375 | 1125 | 750 | 3 | 789.0547 | 711.5313 | Shared Network Asset | 70.14% | 4 | 11.61% | 4
Substation 5 | 330/138.6/11 | 4 | 375/400/400/375 | 1550 | 1150 | 4 | 714.4595 | 644.2649 | Shared Network Asset | 46.09% | 5 | 12.05% | 5
Substation 6 | 330/138.6/11 | 1 | 375 | 375 | 0 | 1 | 106.9653 | 96.4561 | Shared Network Asset | 28.52% | 6 | 13.93% | 6
Substation 7 | 330/220/33 | 2 | 200/200 | 400 | 200 | 2 | 45.4251 | 40.9621 | Shared Network Asset | 11.36% | 7 | 15.16% | 7
Substation 8 | 330/138.6/11 | 2 | 280/280 | 560 | 280 | 2 | 84.8705 | 76.5321 | Shared Network Asset | 15.16% | 8 | 15.19% | 8
Substation 9 | 525/345/34.5 | 1 | 1200 | 1200 | 0 | 1 | 561.9187 | 506.711 | Shared Network Asset | 46.83% | 9 | 16.88% | 9
Substation 10 | 330/138.6/11 | 3 | 400/400/400 | 1200 | 800 | 3 | 525.1225 | 473.53 | Shared Network Asset | 43.76% | 10 | 18.5% | 10
Substation 11 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 257.8095 | 232.4801 | Shared Network Asset | 34.37% | 11 | 20.35% | 11
Substation 12 | 525/345/34.5 | 2 | 1200/1200 | 2400 | 1200 | 2 | 1010.1453 | 910.9001 | Shared Network Asset | 42.09% | 12 | 21.79% | 12
Substation 13 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 104.5097 | 94.2418 | Shared Network Asset | 13.93% | 13 | 28.52% | 13
Substation 14 | 330/138.6/11 | 1 | 375 | 375 | 0 | 1 | 63.2826 | 57.0651 | Shared Network Asset | 16.88% | 14 | 31.39% | 14
Substation 15 | 525/345/34.5 | 2 | 1500/1500 | 3000 | 1500 | 2 | 190.7781 | 172.0344 | Shared Network Asset | 6.359% | 15 | 31.52% | 15
Substation 16 | 330/138.6/11 | 1 | 375 | 375 | 0 | 1 | 173.7226 | 156.6546 | Shared Network Asset | 46.33% | 16 | 33.82% | 16
Substation 17 | 330/132/11 | 2 | 40/40 | 80 | 40 | 2 | 65.6182 | 59.1713 | Shared Network Asset | 82.02% | 17 | 34.37% | 17
Substation 18 | 330/138.6/11 | 4 | 375/375/375/375 | 1500 | 1125 | 4 | 952.5192 | 858.9357 | Shared Network Asset | 63.5% | 18 | 37.05% | 18
Substation 19 | 330/138.6/11 | 3 | 400/400/400 | 1200 | 800 | 3 | 774.8007 | 698.6778 | Shared Network Asset | 64.57% | 19 | 37.98% | 19
Substation 20 | 330/138.6/11 | 5 | 375/375/375/375/375 | 1875 | 1500 | 5 | 975.0271 | 879.2322 | Shared Network Asset | 52% | 20 | 38.16% | 20
Substation 21 | 330/138.6/11 | 6 | 375/375/375/375/375/375 | 2250 | 1875 | 6 | 1270.5781 | 1145.7458 | Shared Network Asset | 56.47% | 21 | 38.28% | 21
Substation 22 | 330/138.6/11 | 3 | 200/150/150 | 500 | 300 | 3 | 190.7832 | 172.039 | Shared Network Asset | 38.16% | 22 | 42.09% | 22
Substation 23 | 330/138.6/11 | 3 | 375/375/375 | 1125 | 750 | 3 | 354.5474 | 319.7137 | Shared Network Asset | 31.52% | 23 | 43.76% | 23
Substation 24 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 287.0674 | 258.8635 | Shared Network Asset | 38.28% | 24 | 46.09% | 24
Substation 25 | 330/138.6/11 | 2 | 200/200 | 400 | 200 | 2 | 73.988 | 66.7188 | Shared Network Asset | 18.5% | 25 | 46.33% | 25
Substation 26 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 113.9535 | 102.7577 | Shared Network Asset | 15.19% | 26 | 46.83% | 26
Substation 27 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 235.4096 | 212.2809 | Shared Network Asset | 31.39% | 27 | 52% | 27
Substation 28 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 277.9 | 250.5968 | Shared Network Asset | 37.05% | 28 | 56.47% | Mean
Substation 29 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 253.6288 | 228.7101 | Shared Network Asset | 33.82% | 29 | 63.5%
Substation 30 | 330/138.6/11 | 2 | 375/375 | 750 | 375 | 2 | 152.5911 | 137.5992 | Shared Network Asset | 20.35% | 30 | 64.57%
Substation 31 | 525/345/34.5 | 1 | 1500 | 1500 | 0 | 1 | 139.1439 | 125.4733 | Shared Network Asset | 9.276% | 31 | 70.14%
Substation 32 | 330/138.6/11 | 2 | 200/200 | 400 | 200 | 2 | 46.4589 | 41.8944 | Shared Network Asset | 11.61% | 32 | 82.02%
|  |  |  | 1129.375 | [5 empty] | 34.29% | Mean | 34.29%
Note on D5: p73300: MVA Rating of primary winding for each transformer. Ex. MVA Txf1/MVA Txf2/MVA Txf3/MVA Txf4

## Lines
Notes:
Lines >=110KV only
Ratings ratings should be nominal based on "nominal" wind / temperature design
Summer
Line | Voltage | Length - km | Nominal Rating | Limiting factor (Summer) | Non Thermal Rating Constraints | Summer Peak Load | Customer Connection/Shared Network Asset
|  |  | Summer (MVA) |  | Yes / No | MVA |  |  |  | Summer
Line 1 | 500 | 143.31 | 1039 | S | Yes | 519.2018 | Shared Network Asset | 49.97% | 1 | 2.401%
Line 2 | 500 | 143.31 | 1039 | S | Yes | 519.2018 | Shared Network Asset | 49.97% | 2 | 2.49%
Line 3 | 500 | 226.63 | 3289 | L | No | 154.1885 | Shared Network Asset | 4.688% | 3 | 2.49%
Line 4 | 500 | 114.09 | 3239 | L | No | 190.8645 | Shared Network Asset | 5.893% | 4 | 2.85%
Line 5 | 500 | 112.54 | 3239 | L | No | 77.7613 | Shared Network Asset | 2.401% | 5 | 3.017%
Line 6 | 500 | 141.6 | 3281 | L | No | 81.7063 | Shared Network Asset | 2.49% | 6 | 3.017%
Line 7 | 500 | 141.6 | 3281 | L | No | 81.7063 | Shared Network Asset | 2.49% | 7 | 3.831%
Line 8 | 330 | 99.859 | 915 | L | Yes/Stability | 782.2759 | Shared Network Asset | 85.49% | 8 | 4.456%
Line 9 | 330 | 148.92 | 915 | L | Yes/Stability | 619.3329 | Shared Network Asset | 67.69% | 9 | 4.688%
Line 10 | 330 | 128.847 | 972 | L | No | 853.9563 | Shared Network Asset | 87.86% | 10 | 5.81%
Line 11 | 330 | 113.82 | 697 | L | No | 644.6178 | Shared Network Asset | 92.48% | 11 | 5.893%
Line 12 | 330 | 118.066 | 697 | L | No | 620.9802 | Shared Network Asset | 89.09% | 12 | 5.927%
Line 13 | 330 | 60.255 | 915 | L | No | 500.7855 | Shared Network Asset | 54.73% | 13 | 5.932%
Line 14 | 330 | 98.76 | 972 | L | Yes/Stability | 948.5419 | Shared Network Asset | 97.59% | 14 | 5.933%
Line 15 | 330 | 70.755 | 915 | L | No | 497.0302 | Shared Network Asset | 54.32% | 15 | 6.3%
Line 16 | 330 | 42.18 | 915 | L | Yes/Stability | 351.879 | Shared Network Asset | 38.46% | 16 | 6.748%
Line 17 | 330 | 10.87 | 1260 | S | Yes | 112.5145 | Shared Network Asset | 8.93% | 17 | 8.284%
Line 18 | 330 | 68 | 1280 | L | No | 818.9268 | Shared Network Asset | 63.98% | 18 | 8.881%
Line 19 | 330 | 18.27 | 1215 | L | No | 461.475 | Shared Network Asset | 37.98% | 19 | 8.93%
Line 20 | 330 | 24.099 | 1215 | L | No | 833.7154 | Shared Network Asset | 68.62% | 20 | 9.699%
Line 21 | 330 | 49.761 | 1215 | L | No | 665.6052 | Shared Network Asset | 54.78% | 21 | 10.03%
Line 22 | 330 | 70.63 | 915 | L | No | 509.2301 | Shared Network Asset | 55.65% | 22 | 11.22%
Line 23 | 330 | 47.977 | 1280 | L | No | 588.8565 | Shared Network Asset | 46% | 23 | 11.29%
Line 24 | 330 | 42.7 | 915 | L | No | 609.8865 | Shared Network Asset | 66.65% | 24 | 11.42%
Line 25 | 330 | 33.204 | 1215 | L | No | 274.8268 | Shared Network Asset | 22.62% | 25 | 11.44%
Line 26 | 330 | 64.545 | 1215 | L | No | 306.1183 | Shared Network Asset | 25.19% | 26 | 11.61%
Line 27 | 330 | 86.05 | 1143 | D | Yes | 514.5728 | Shared Network Asset | 45.02% | 27 | 11.62%
Line 28 | 330 | 7.175 | 1215 | L | No | 324.6806 | Shared Network Asset | 26.72% | 28 | 11.7%
Line 29 | 330 | 30.134 | 1143 | D | Yes | 338.344 | Shared Network Asset | 29.6% | 29 | 11.99%
Line 30 | 330 | 109.439 | 1215 | L | No | 416.0734 | Shared Network Asset | 34.24% | 30 | 12.5%
Line 31 | 330 | 124.14 | 1215 | L | No | 293.1428 | Shared Network Asset | 24.13% | 31 | 12.66%
Line 32 | 330 | 21.907 | 1215 | L | No | 402.5969 | Shared Network Asset | 33.14% | 32 | 13.25%
Line 33 | 330 | 22.335 | 1215 | L | No | 382.406 | Shared Network Asset | 31.47% | 33 | 13.35%
Line 34 | 330 | 20.651 | 1215 | L | No | 183.5462 | Shared Network Asset | 15.11% | 34 | 13.8%
Line 35 | 330 | 39.922 | 1215 | L | No | 582.2888 | Shared Network Asset | 47.93% | 35 | 13.81%
Line 36 | 330 | 16.64 | 1215 | L | No | 107.9084 | Shared Network Asset | 8.881% | 36 | 15.11%
Line 37 | 330 | 171.001 | 1210 | P | Yes | 539.999 | Shared Network Asset | 44.63% | 37 | 15.2%
Line 38 | 330 | 188.501 | 844 | P | Yes | 510.9418 | Shared Network Asset | 60.54% | 38 | 15.38%
Line 39 | 330 | 6.031 | 1215 | L | No | 725.2334 | Shared Network Asset | 59.69% | 39 | 15.42%
Line 40 | 330 | 6.031 | 1215 | L | No | 721.0151 | Shared Network Asset | 59.34% | 40 | 15.76%
Line 41 | 330 | 20 | 1220 | L | No | 141.7061 | Shared Network Asset | 11.62% | 41 | 16.32%
Line 42 | 330 | 19.981 | 1220 | L | No | 141.7011 | Shared Network Asset | 11.61% | 42 | 16.32%
Line 43 | 330 | 16.336 | 1280 | L | No | 534.5171 | Shared Network Asset | 41.76% | 43 | 16.37%
Line 44 | 330 | 17.5 | 1143 | S | Yes | 286.6656 | Shared Network Asset | 25.08% | 44 | 16.73%
Line 45 | 330 | 110.23 | 915 | L | No | 843.8955 | Shared Network Asset | 92.23% | 45 | 17.95%
Line 46 | 330 | 130.534 | 915 | L | No | 502.3672 | Shared Network Asset | 54.9% | 46 | 18.44%
Line 47 | 330 | 19.7 | 575 | 0 | Yes | 505 | Shared Network Asset | 87.83% | 47 | 18.66%
Line 48 | 330 | 27.5 | 750 | 0 | Yes | 620.6411 | Shared Network Asset | 82.75% | 48 | 18.75%
Line 49 | 330 | 100.44 | 983 | L | Yes/Stability | 43.8046 | Shared Network Asset | 4.456% | 49 | 19.41%
Line 50 | 330 | 42.36 | 915 | L | Yes/Stability | 199.2819 | Shared Network Asset | 21.78% | 50 | 19.51%
Line 51 | 330 | 43.55 | 915 | L | No | 599.7408 | Shared Network Asset | 65.55% | 51 | 20.04%
Line 52 | 330 | 99.603 | 915 | L | Yes/Stability | 57.6442 | Shared Network Asset | 6.3% | 52 | 20.06%
Line 53 | 330 | 151.657 | 569 | P | Yes | 106.6722 | Shared Network Asset | 18.75% | 53 | 20.32%
Line 54 | 330 | 40.601 | 714 | 0 | Yes | 257.3695 | Shared Network Asset | 36.05% | 54 | 21.77%
Line 55 | 330 | 45.528 | 715 | L | Yes/Stability | 500.5178 | Shared Network Asset | 70% | 55 | 21.78%
Line 56 | 330 | 73.039 | 715 | L | Yes/Stability | 177.4406 | Shared Network Asset | 24.82% | 56 | 22.02%
Line 57 | 330 | 7.868 | 1239 | L | No | 592.1059 | Shared Network Asset | 47.79% | 57 | 22.23%
Line 58 | 330 | 7.868 | 1239 | L | No | 592.106 | Shared Network Asset | 47.79% | 58 | 22.62%
Line 59 | 330 | 171.01 | 915 | S | Yes | 121.2673 | Shared Network Asset | 13.25% | 59 | 22.77%
Line 60 | 330 | 142.813 | 1215 | L | No | 729.372 | Shared Network Asset | 60.03% | 60 | 23.31%
Line 61 | 330 | 121.424 | 1215 | L | No | 752.6011 | Shared Network Asset | 61.94% | 61 | 23.73%
Line 62 | 330 | 21.131 | 1215 | L | No | 589.5724 | Shared Network Asset | 48.52% | 62 | 24.13%
Line 63 | 330 | 116.878 | 915 | S | Yes | 141.1127 | Shared Network Asset | 15.42% | 63 | 24.82%
Line 64 | 330 | 100.82 | 1215 | L | No | 538.7828 | Shared Network Asset | 44.34% | 64 | 24.93%
Line 65 | 330 | 118.416 | 1215 | L | No | 526.4341 | Shared Network Asset | 43.33% | 65 | 25.08%
Line 66 | 330 | 17.675 | 983 | L | No | 698.0386 | Shared Network Asset | 71.01% | 66 | 25.19%
Line 67 | 330 | 139.483 | 983 | L | No | 705.6159 | Shared Network Asset | 71.78% | 67 | 25.47%
Line 68 | 330 | 103.67 | 892 | L | No | 603.2475 | Shared Network Asset | 67.63% | 68 | 25.51%
Line 69 | 330 | 110.871 | 840 | L | No | 570.8494 | Shared Network Asset | 67.96% | 69 | 26.47%
Line 70 | 330 | 135.291 | 756 | S | Yes | 200.0802 | Shared Network Asset | 26.47% | 70 | 26.55%
Line 71 | 330 | 126.853 | 892 | L | No | 681.8375 | Shared Network Asset | 76.44% | 71 | 26.72%
Line 72 | 330 | 172.651 | 892 | L | No | 112.9384 | Shared Network Asset | 12.66% | 72 | 27.27%
Line 73 | 330 | 172 | 1097 | S | Yes/Stability | 385.4629 | Shared Network Asset | 35.14% | 73 | 27.97%
Line 74 | 330 | 172 | 1097 | S | Yes/Stability | 384.8834 | Shared Network Asset | 35.09% | 74 | 28.48%
Line 75 | 330 | 21.149 | 1215 | L | No | 691.3786 | Shared Network Asset | 56.9% | 75 | 29.29%
Line 76 | 330 | 35.919 | 1097 | S | Yes | 131.5293 | Shared Network Asset | 11.99% | 76 | 29.29%
Line 77 | 330 | 20.708 | 1215 | L | No | 669.1409 | Shared Network Asset | 55.07% | 77 | 29.6%
Line 78 | 330 | 24.257 | 1215 | L | No | 339.8088 | Shared Network Asset | 27.97% | 78 | 29.92%
Line 79 | 330 | 25.365 | 1215 | L | No | 322.5932 | Shared Network Asset | 26.55% | 79 | 30.56%
Line 80 | 330 | 17.788 | 1215 | L | No | 398.1457 | Shared Network Asset | 32.77% | 80 | 31.47%
Line 81 | 330 | 8.771 | 1215 | L | No | 162.2246 | Shared Network Asset | 13.35% | 81 | 32.17%
Line 82 | 220 | 23.904 | 265 | B | Yes/Stability | 30.2762 | Shared Network Asset | 11.42% | 82 | 32.2%
Line 83 | 220 | 259.462 | 95 | S | Yes | 54.4223 | Shared Network Asset | 57.29% | 83 | 32.77%
Line 84 | 220 | 249.802 | 301 | P | Yes | 47.4308 | Shared Network Asset | 15.76% | 84 | 33.14%
Line 85 | 220 | 148.004 | 227 | P | Yes | 42.3686 | Shared Network Asset | 18.66% | 85 | 33.95%
Line 86 | 330 | 0.4 | 1500 | 0 | Yes | 207.1489 | Shared Network Asset | 13.81% | 86 | 34.24%
Line 87 | 330 | 0.4 | 1500 | 0 | Yes | 207.0407 | Shared Network Asset | 13.8% | 87 | 34.27%
Line 88 | 132 | 89.285 | 122 | L | No | 84.6572 | Shared Network Asset | 69.39% | 88 | 34.45%
Line 89 | 132 | 18.925 | 122 | L | No | 86.9403 | Shared Network Asset | 71.26% | 89 | 34.48%
Line 90 | 132 | 66 | 137 | L | No | 59.7349 | Shared Network Asset | 43.6% | 90 | 34.66%
Line 91 | 132 | 138.735 | 106 | L | No | 36.744 | Shared Network Asset | 34.66% | 91 | 35.09%
Line 92 | 132 | 177 | 105 | L | No | 26.1778 | Shared Network Asset | 24.93% | 92 | 35.14%
Line 93 | 132 | 90.166 | 122 | L | No | 4.6739 | Shared Network Asset | 3.831% | 93 | 36.05%
Line 94 | 132 | 174.029 | 122 | L | No | 39.2888 | Shared Network Asset | 32.2% | 94 | 37.75%
Line 95 | 132 | 65.274 | 86 | L | No | 47.0832 | Shared Network Asset | 54.75% | 95 | 37.84%
Line 96 | 132 | 99.762 | 110 | P | Yes | 28.0659 | Shared Network Asset | 25.51% | 96 | 37.98%
Line 97 | 132 | 40.012 | 110 | P | Yes | 28.0143 | Shared Network Asset | 25.47% | 97 | 38.4%
Line 98 | 132 | 31.495 | 112 | L | No | 107.2883 | Shared Network Asset | 95.79% | 98 | 38.46%
Line 99 | 132 | 43.182 | 158 | L | No | 9.3722 | Shared Network Asset | 5.932% | 99 | 39.89%
Line 100 | 132 | 80.03 | 122 | L | No | 21.8952 | Shared Network Asset | 17.95% | 100 | 40.82%
Line 101 | 132 | 110.804 | 122 | L | No | 12.2375 | Shared Network Asset | 10.03% | 101 | 41.68%
Line 102 | 132 | 14.6 | 114 | S | Yes | 14.2472 | Shared Network Asset | 12.5% | 102 | 41.76%
Line 103 | 132 | 107.219 | 96 | P | Yes | 22.7856 | Shared Network Asset | 23.73% | 103 | 42.12%
Line 104 | 132 | 111.189 | 110 | P | Yes | 17.9499 | Shared Network Asset | 16.32% | 104 | 42.92%
Line 105 | 132 | 85.85 | 112 | L | No | 71.3235 | Shared Network Asset | 63.68% | 105 | 43.33%
Line 106 | 132 | 80.512 | 93 | P | Yes | 15.1772 | Shared Network Asset | 16.32% | 106 | 43.6%
Line 107 | 132 | 96.259 | 122 | L | No | 22.5022 | Shared Network Asset | 18.44% | 107 | 44.34%
Line 108 | 132 | 3.03 | 133 | L | No | 55.4285 | Shared Network Asset | 41.68% | 108 | 44.63%
Line 109 | 132 | 3.207 | 144 | H | Yes | 60.6584 | Shared Network Asset | 42.12% | 109 | 44.8%
Line 110 | 132 | 143 | 101 | S | Yes | 6.8155 | Shared Network Asset | 6.748% | 110 | 45.02%
Line 111 | 132 | 98.904 | 86 | L | No | 29.1939 | Shared Network Asset | 33.95% | 111 | 45.38%
Line 112 | 132 | 67.76 | 122 | L | No | 3.4765 | Shared Network Asset | 2.85% | 112 | 46%
Line 113 | 132 | 77.519 | 114 | L | No | 12.7887 | Shared Network Asset | 11.22% | 113 | 47.79%
Line 114 | 132 | 25.297 | 138 | H | Yes | 21.2269 | Shared Network Asset | 15.38% | 114 | 47.79%
Line 115 | 132 | 45.427 | 115 | L | No | 6.6811 | Shared Network Asset | 5.81% | 115 | 47.93%
Line 116 | 132 | 13.311 | 115 | L | No | 12.9835 | Shared Network Asset | 11.29% | 116 | 48.2%
Line 117 | 132 | 36.234 | 159 | L | No | 18.1878 | Shared Network Asset | 11.44% | 117 | 48.2%
Line 118 | 132 | 13.338 | 159 | L | No | 31.865 | Shared Network Asset | 20.04% | 118 | 48.52%
Line 119 | 132 | 43.182 | 158 | L | No | 9.3648 | Shared Network Asset | 5.927% | 119 | 49.97%
Line 120 | 132 | 12.57 | 243 | L | No | 48.7346 | Shared Network Asset | 20.06% | 120 | 49.97%
Line 121 | 132 | 97.227 | 97 | L | No | 41.6336 | Shared Network Asset | 42.92% | 121 | 50.44%
Line 122 | 132 | 60.139 | 112 | L | No | 24.8921 | Shared Network Asset | 22.23% | 122 | 50.76%
Line 123 | 132 | 6.15 | 112 | L | No | 104.949 | Shared Network Asset | 93.7% | 123 | 53.47%
Line 124 | 132 | 19.003 | 50 | 0 | Yes | 31.7654 | Shared Network Asset | 63.53% | 124 | 54.2%
Line 125 | 132 | 70.007 | 134 | L | No | 30.5098 | Shared Network Asset | 22.77% | 125 | 54.32%
Line 126 | 132 | 44.243 | 134 | L | No | 26.0034 | Shared Network Asset | 19.41% | 126 | 54.73%
Line 127 | 132 | 94.95 | 134 | L | No | 53.4564 | Shared Network Asset | 39.89% | 127 | 54.75%
Line 128 | 132 | 52.24 | 134 | L | No | 27.2233 | Shared Network Asset | 20.32% | 128 | 54.78%
Line 129 | 132 | 9 | 219 | S | Yes | 111.1635 | Shared Network Asset | 50.76% | 129 | 54.9%
Line 130 | 132 | 116.655 | 114 | S | Yes | 13.333 | Shared Network Asset | 11.7% | 130 | 55.07%
Line 131 | 132 | 42.666 | 134 | L | No | 40.0917 | Shared Network Asset | 29.92% | 131 | 55.65%
Line 132 | 132 | 29.609 | 134 | L | No | 11.1002 | Shared Network Asset | 8.284% | 132 | 56.9%
Line 133 | 132 | 52.225 | 134 | L | No | 26.1453 | Shared Network Asset | 19.51% | 133 | 57.29%
Line 134 | 132 | 26.584 | 101 | S | Yes | 5.9919 | Customer Connection Asset | 5.933% | 134 | 59.1%
Line 135 | 132 | 29.373 | 112 | L | No | 18.739 | Shared Network Asset | 16.73% | 135 | 59.34%
Line 136 | 132 | 30.278 | 114 | S | Yes | 46.5369 | Shared Network Asset | 40.82% | 136 | 59.69%
Line 137 | 132 | 57.11 | 134 | L | No | 72.6276 | Shared Network Asset | 54.2% | 137 | 60.03%
Line 138 | 132 | 1.75 | 407 | L | No | 182.3553 | Shared Network Asset | 44.8% | 138 | 60.36%
Line 139 | 132 | 88.23 | 91 | S | Yes | 81.131 | Shared Network Asset | 89.15% | 139 | 60.36%
Line 140 | 132 | 37.252 | 91 | W | Yes | 56.3105 | Shared Network Asset | 61.88% | 140 | 60.54%
Line 141 | 132 | 118.98 | 125 | L | No | 56.7223 | Shared Network Asset | 45.38% | 141 | 61.88%
Line 142 | 132 | 30.11 | 76 | P | Yes | 36.6315 | Shared Network Asset | 48.2% | 142 | 61.94%
Line 143 | 132 | 27.38 | 76 | P | Yes | 36.6314 | Shared Network Asset | 48.2% | 143 | 63.53%
Line 144 | 132 | 27.38 | 125 | L | No | 36.6141 | Shared Network Asset | 29.29% | 144 | 63.68%
Line 145 | 132 | 30.14 | 125 | L | No | 36.6142 | Shared Network Asset | 29.29% | 145 | 63.98%
Line 146 | 132 | 73.356 | 80 | P | Yes | 30.1984 | Shared Network Asset | 37.75% | 146 | 63.99%
Line 147 | 132 | 79.615 | 183 | L | No | 27.8076 | Shared Network Asset | 15.2% | 147 | 65.55%
Line 148 | 132 | 18.9 | 69 | L | No | 63.5237 | Shared Network Asset | 92.06% | 148 | 66.65%
Line 149 | 132 | 18.25 | 41 | L | No | 35 | Shared Network Asset | 85.37% | 149 | 67.63%
Line 150 | 132 | 66.01 | 101 | P | Yes | 3.0471 | Shared Network Asset | 3.017% | 150 | 67.69%
Line 151 | 132 | 12.238 | 101 | P | Yes | 3.0472 | Shared Network Asset | 3.017% | 151 | 67.96%
Line 152 | 132 | 150.297 | 114 | S | Yes | 80.5778 | Shared Network Asset | 70.68% | 152 | 68.62%
Line 153 | 132 | 112.508 | 125 | L | No | 79.9832 | Shared Network Asset | 63.99% | 153 | 69.39%
Line 154 | 132 | 52.68 | 114 | S | Yes | 57.4959 | Shared Network Asset | 50.44% | 154 | 70%
Line 155 | 132 | 79.573 | 114 | S | Yes | 97.127 | Shared Network Asset | 85.2% | 155 | 70.68%
Line 156 | 132 | 127.73 | 125 | L | No | 27.5197 | Shared Network Asset | 22.02% | 156 | 71.01%
Line 157 | 132 | 106 | 125 | L | No | 38.2038 | Shared Network Asset | 30.56% | 157 | 71.26%
Line 158 | 132 | 114.49 | 36 | L | No | 31 | Shared Network Asset | 86.11% | 158 | 71.78%
Line 159 | 132 | 167.337 | 125 | L | No | 43.0567 | Shared Network Asset | 34.45% | 159 | 72.62%
Line 160 | 132 | 16.956 | 256 | L | No | 88.2635 | Shared Network Asset | 34.48% | 160 | 73.84%
Line 161 | 132 | 37.401 | 114 | S | Yes | 24.8227 | Shared Network Asset | 21.77% | 161 | 76.44%
Line 162 | 132 | 109.1 | 114 | S | Yes | 60.9531 | Shared Network Asset | 53.47% | 162 | 77.05%
Line 163 | 132 | 11.467 | 214 | S | Yes | 82.1664 | Shared Network Asset | 38.4% | 163 | 82.75%
Line 164 | 132 | 45.89 | 125 | L | No | 42.8401 | Shared Network Asset | 34.27% | 164 | 84.42%
Line 165 | 132 | 59.66 | 114 | S | Yes | 43.1433 | Shared Network Asset | 37.84% | 165 | 84.92%
Line 166 | 132 | 152.66 | 114 | S | Yes | 11.0574 | Shared Network Asset | 9.699% | 166 | 85.2%
Line 167 | 132 | 71.916 | 125 | L | No | 40.2125 | Shared Network Asset | 32.17% | 167 | 85.37%
Line 168 | 132 | 8.206 | 114 | S | Yes | 67.3795 | Shared Network Asset | 59.1% | 168 | 85.49%
Line 169 | 132 | 13.34 | 125 | L | No | 20.4581 | Shared Network Asset | 16.37% | 169 | 86.11%
Line 170 | 132 | 9.801 | 168 | L | No | 122.0025 | Shared Network Asset | 72.62% | 170 | 87.81%
Line 171 | 132 | 10.307 | 137 | W | Yes | 116.3346 | Shared Network Asset | 84.92% | 171 | 87.83%
Line 172 | 132 | 9.721 | 224 | L | No | 61.0896 | Shared Network Asset | 27.27% | 172 | 87.86%
Line 173 | 132 | 16.857 | 512 | L | No | 309.0506 | Shared Network Asset | 60.36% | 173 | 89.09%
Line 174 | 132 | 16.857 | 512 | L | No | 309.0506 | Shared Network Asset | 60.36% | 174 | 89.15%
Line 175 | 132 | 46.626 | 125 | L | No | 29.1424 | Shared Network Asset | 23.31% | 175 | 89.97%
Line 176 | 132 | 12.226 | 125 | L | No | 112.4601 | Shared Network Asset | 89.97% | 176 | 92.06%
Line 177 | 132 | 7.862 | 125 | L | No | 35.6032 | Shared Network Asset | 28.48% | 177 | 92.23%
Line 178 | 330 | 5.634 | 206 | S | Yes | 173.9045 | Shared Network Asset | 84.42% | 178 | 92.48%
Line 179 | 330 | 5.428 | 206 | S | Yes | 180.8857 | Shared Network Asset | 87.81% | 179 | 93.7%
Line 180 | 330 | 3.908 | 206 | S | Yes | 158.7308 | Shared Network Asset | 77.05% | 180 | 95.79%
Line 181 | 330 | 4.071 | 206 | S | Yes | 152.1042 | Shared Network Asset | 73.84% | 181 | 97.59%
|  | 12294.431 | 624.3812 |  |  | 41558.6974 |  |  | Mean | 40.08%
|  |  |  | In tabular listings, the description of the equipment limiting the rating has been abbreviated to a single standard character as follows: |  |  |  |  | 53 | 19%
|  |  |  | L | Overhead transmission line thermal rating |  |  |  | 181 | 181%
|  |  |  | U | Underground cable rating |  |  |  | 0.29282 | 0.10497
|  |  |  | T | Transformer (tail-ended circuit)
|  |  |  | B | Breaker
|  |  |  | D | Disconnector
|  |  |  | H | High voltage connections
|  |  |  | C | Primary of CT
|  |  |  | S | Secondary of CT (protection metering or indication)
|  |  |  | P | Protection trip setting
|  |  |  | W | Wave traps
Note on E5: p73300: Key shown in Cell F210