## Substations
Notes:
Substations with a Primary Voltage >=110KV only
Transformers ratings should be nominal nameplate at highest continuous rating - i.e with pumps / fans on where applicable
Substation | Voltage Ratio |  | Number of Transformers | Transformer Ratings |  |  |  | "N" Rating | "N-1" Rating | Summer Peak Load * | * Load at 1500hrs 18/1/2010 - date / time of last Summer network maximum demand (8891 MW).
|  |  |  | MVA |  |  |  | MVA | MVA | MVA
Substation 1 | 275 | 110 | 2 | 250 | 200 |  |  | 450 | 200 | 157 | 0.5 | 34.89% | 1 | 6.933%
Substation 2 | 275 | 110 | 2 | 250 | 375 |  |  | 625 | 250 | 306 | 0.5 | 48.96% | 2 | 10.8%
Substation 3 | 275 | 110 | 3 | 375 | 375 | 375 |  | 1125 | 750 | 711 | 0.67 | 63.2% | 3 | 12%
Substation 4 | 275 | 110 | 4 | 250 | 250 | 375 | 375 | 1250 | 875 | 531 | 0.75 | 42.48% | 4 | 12.77%
Substation 5 | 275 | 110 | 3 | 250 | 250 | 250 |  | 750 | 500 | 376 | 0.67 | 50.13% | 5 | 14.75%
Substation 6 | 275 | 132 | 3 | 120 | 120 | 275 |  | 515 | 240 | 196 | 0.67 | 38.06% | 6 | 15.47%
Substation 7 | 275 | 132 | 2 | 250 | 250 |  |  | 500 | 250 | 140 | 0.5 | 28% | 7 | 15.56%
Substation 8 | 275 | 132 | 2 | 300 | 300 |  |  | 600 | 300 | 180 | 0.5 | 30% | 8 | 16.86%
Substation 9 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 343 | 0.5 | 45.73% | 9 | 19.56%
Substation 10 | 132/ | 110 | 3 | 120 | 140 |  |  | 260 | 120 | 76 | 0.67 | 29.23% | 10 | 25.47%
Substation 11 | 275 | 132 | 3 | 200 | 200 |  |  | 400 | 200 | 162 | 0.67 | 40.5% | 11 | 28%
Substation 12 | 275 | 132 | 3 | 200 | 200 | 250 |  | 650 | 400 | 338 | 0.67 | 52% | 12 | 29.07%
Substation 13 | 275 | 132 | 3 | 250 | 250 | 250 |  | 750 | 500 | 116 | 0.67 | 15.47% | 13 | 29.23%
Substation 14 | 275 | 110 | 3 | 250 | 200 | 200 |  | 650 | 400 | 83 | 0.67 | 12.77% | 14 | 30%
Substation 15 | 330 | 275 | 2 | 1500 | 1500 |  |  | 3000 | 1500 | 1189 | 0.5 | 39.63% | 15 | 34.89%
Substation 16 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 218 | 0.5 | 29.07% | 16 | 38.06%
Substation 17 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 427 | 0.5 | 56.93% | 17 | 39.63%
Substation 18 | 275 | 132 | 2 | 90 | 90 |  |  | 180 | 90 | 28 | 0.5 | 15.56% | 18 | 40.5%
Substation 19 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 421 | 0.5 | 56.13% | 19 | 42.48%
Substation 20 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 447 | 0.5 | 59.6% | 20 | 45.73%
Substation 21 | 275 | 132 | 1 | 250 |  |  |  | 250 | 0 | 146 |  | 58.4% | 21 | 48.96%
Substation 22 | 275 | 110 | 2 | 375 | 375 |  |  | 750 | 375 | 435 | 0.5 | 58% | 22 | 49.6%
Substation 23 | 275 | 132 | 2 | 200 | 200 |  |  | 400 | 200 | 59 | 0.5 | 14.75% | 23 | 50.13%
Substation 24 | 275 | 132 | 1 | 375 |  |  |  | 375 | 0 | 26 |  | 6.933% | 24 | 51.73%
Substation 25 | 275 | 110 | 1 | 375 |  |  |  | 375 | 0 | 186 |  | 49.6% | 25 | 52%
Substation 26 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 191 | 0.5 | 25.47% | 26 | 56.13%
Substation 27 | 275 | 132 | 2 | 375 | 375 |  |  | 750 | 375 | 81 | 0.5 | 10.8% | 27 | 56.93%
Substation 28 | 275 | 110 | 1 | 375 |  |  |  | 375 | 0 | 194 |  | 51.73% | 28 | 58%
Substation 29 | 275 | 132 | 2 | 350 | 350 |  |  | 700 | 350 | 118 | 0.5 | 16.86% | 29 | 58.4%
Substation 30 | 330 | 275 | 2 | 1125 | 1125 |  |  | 2250 | 1125 | 440 | 0.5 | 19.56% | 30 | 59.6%
Substation 31 | 330 | 132 | 1 | 100 |  |  |  | 100 | 0 | 12 |  | 12% | 31 | 63.2%
|  |  | 67 |  |  |  |  | 22530 | 11250 | 8333 | 0.56192 |  | Mean | 35.89%
[8 empty] | 0.36986 | 0.74071 |  |  |  |  | 35.89%
|  |  | 4 |  |  |  |  | 22530 |  |  | 0.75
|  |  | 3 |  |  |  |  | 726.7742 |  |  | 0.67
|  |  | 3 | [7 empty] | 0.67
|  |  | 2 | [7 empty] | 0.5
|  |  | 2 | [7 empty] | 0.5
|  |  | 2 | [7 empty] | 0.5
0.59833